CEMLINE CORPORATION

JST – JACKETED (CEMENT LINED) TANK SPECIFICATION

CEMLINE JST Series, jacketed storage tank shall be factory jacketed and insulated as a pre-packaged unit. The steel storage tank shall be constructed in accordance with Section IV of the ASME Code for 125 psig working pressure. The tank shall be registered with the National Board of Boiler and Pressure Vessel Inspectors and Certificate of Shop Inspection shall be furnished. The tank shall be lined with not less than 1/2" thick STONESTEEL cement lining, and all threaded openings shall be of 304 stainless steel. Tanks above 36" diameter shall have wire mesh completely welded over the interior prior to application of lining. An 11" x 15" manhole shall be furnished as required by ASME Code on tanks above 400-gallon storage capacity. Tank shall be mounted (horizontally on structural support skid) (vertically with leveling bolts and coupling for pipe legs). The tank shall be insulated with 3" dense fiberglass protected by 20 gauge enameled steel jacket. All openings shall be extended through the jacket with red brass nipples. Estucheons shall be used at all jacket penetrations. Jacketed storage tank shall be CEMLINE Model _____JST.

OPTIONAL COIL

Tank shall be furnished with a submerged u-bend coil with 3/4" O.D. copper tubes, copper lined tubesheet, and steel or cast iron coil head. The coil shall be designed to heat ______ GPH from ____ °F to ____  °F with (_____psig steam) (_______ GPM _____ °F boiler water).